DAB Active Driver Plus CAN Reverse Engineering Test Plan.

Objective

The purpose of this test plan is to determine:

- Whether the observed CAN traffic is related to automatic address assignment.

- Whether a master/slave election mechanism exists.

- Whether the captured traffic is discovery / network-management traffic rather than application data.

- How manual addressing (AD.6.5.7) influences CAN communication.

- Which CAN messages affect pump behavior.

- Where the actual pump-control application layer can be found.

Phase 1 – Addressing & Node Identity

Priority: Very High

This phase is based on the DAB documentation describing automatic and manual address assignment in Multi Inverter systems.

Test 1.1 – Automatic Address Assignment

Configuration

AD.6.5.7 = AUTO

Show more lines

Procedure

- Power off the pump.

- Start CAN capture.

- Power on the pump.

- Record at least 30 seconds.

- Repeat 3 times.

Observe

- First CAN IDs after startup

- Traffic timing

- Presence of:

  - 0F 00

  - 0F 03

  - 0F 04

- Number of unique IDs

Goal

Determine:

Does the startup sequence change between boots?

Show more lines

Test 1.2 – Manual Address 1

Configuration

AD.6.5.7 = 1

Show more lines

Procedure

Repeat Test 1.1.

Compare Against

AUTO

Show more lines

Goal

Determine whether address selection affects:

- CAN IDs

- Message patterns

- Startup sequence

Test 1.3 – Manual Address 2

Configuration

AD.6.5.7 = 2

Show more lines

Repeat Test 1.2.

Test 1.4 – Manual Address 3

Configuration

AD.6.5.7 = 3

``

Show more lines

Repeat Test 1.2.

Success Criteria

Any systematic difference proves that:

AD.6.5.7 influences CAN communication.

Show more lines

This would strongly support the address-assignment hypothesis.

Phase 2 – State Machine Discovery

Priority: High

Goal:

Determine when the protocol changes state.

``

Show more lines

Test 2.1 – Pump Start

Procedure

Capture:

Standby

↓

Pump starts

↓

Normal operation

Show more lines

Look For

- New frame types

- New IDs

- Changes in 0F XX values

Test 2.2 – Pump Stop

Procedure

Capture:

Running

↓

Stop

↓

Standby

Show more lines

Look For

- State transitions

- Special frames

- Change in periodic traffic

Test 2.3 – Pressure Setpoint Change

Procedure

Example:

3.0 bar

↓

4.0 bar

Show more lines

Goal

Identify frames carrying configuration changes.

Test 2.4 – Control Mode Change

Example:

Constant Pressure

↔

Proportional Pressure

``

Show more lines

Goal

Identify the application layer.

Phase 3 – Fault and Exception Conditions

Priority: High

Fault conditions often reveal protocol structure quickly.

Test 3.1 – Dry Run Condition

If safely possible:

Create dry-run fault

Show more lines

Observe

- New CAN frames

- Alarm messages

- Changes in frame timing

Test 3.2 – Sensor Fault

If safely possible:

Disconnect pressure sensor

Show more lines

Observe

- Error codes

- CAN traffic changes

Test 3.3 – CAN Bus Disconnect

Procedure

Capture:

Bus connected

Show more lines

Then:

CAN H / CAN L disconnected

Show more lines

Goal

Determine whether the inverter actively expects network responses.

Phase 4 – Passive Discovery via CAN Injection

Priority: Medium

Goal:

Determine whether the pump reacts to additional nodes.

Show more lines

Test 4.1 – Fake Node Advertisement

Transmit:

ID 00011234

DATA 01 00 00 0F 03 34 12

ID 00111234

DATA 01 00 00 34 12

Show more lines

Observe

- Timing changes

- New message types

- Protocol state changes

Test 4.2 – Multiple Fake Nodes

Transmit:

00011111

00012222

00013333

00014444

Show more lines

Goal

Attempt to trigger:

- Enumeration

- Address assignment

- Master election

Test 4.3 – Alternative Status Values

Transmit:

01 00 00 0F 00 xx xx

Show more lines

Then:

01 00 00 0F 04 xx xx

Show more lines

Goal

Since these values already occur rarely on the bus, they may represent valid protocol states.

Phase 5 – Collision and Validation Tests

Priority: Medium

Goal:

Determine whether IDs are being validated.

Show more lines

Test 5.1 – Duplicate Active ID

When the pump transmits:

00018B5A

Show more lines

Inject:

00018B5A

01 00 00 0F 03 5A 8B

Show more lines

slightly before the pump normally does.

Observe

- Sequence restart

- New IDs

- Error behavior

Test 5.2 – Broken Mirror Payload

Normal frame:

ID 00018B5A

DATA 01 00 00 0F 03 5A 8B

Show more lines

Inject:

ID 00018B5A

DATA 01 00 00 0F 03 AA 55

Show more lines

Goal

Check whether payload consistency is verified.

Test 5.3 – Fixed-ID Repetition

Transmit repeatedly:

ID 00015555

DATA 01 00 00 0F 03 55 55

Show more lines

at 5 ms intervals.

Goal

Determine whether uniqueness of IDs matters.

Phase 6 – Search for the Application Layer

Priority: Very High

Current evidence suggests the captured traffic may be:

Network management

Show more lines

instead of:

Pump control data

Show more lines

Test 6.1 – Minimum vs Maximum Flow

Capture:

Pump idle

↓

Maximum flow

↓

Pump idle

``

Show more lines

Goal

Determine whether any CAN messages correlate with hydraulic activity.

Test 6.2 – Power Consumption Changes

Capture:

Low load

↓

High load

Show more lines

Goal

Look for:

- Current

- Power

- Speed

- Pressure telemetry

Test 6.3 – Menu Navigation

Capture while navigating menus.

Goal

Identify configuration messages.

Phase 7 – Statistical Analysis

Priority: After Data Collection

Once approximately 10–20 captures have been collected:

Analyze

- ID entropy

- Repetition period

- Correlation with address setting

- PRNG behavior

- LFSR behavior

- Startup sequence consistency

- Effects of manual address selection

Goal

Determine whether the identifier stream is:

Random

Show more lines

Pseudo-random

Show more lines

Address-derived

Show more lines

Election-related

Show more lines

Recommended Execution Order

Test 1

- AD.6.5.7 = AUTO

- AD.6.5.7 = 1

- AD.6.5.7 = 2

- AD.6.5.7 = 3

Test 2

- Start/Stop captures

- Setpoint changes

- Mode changes

Test 3

- Fault conditions

- CAN disconnected tests

Test 4

- Safe discovery probes

- Fake node tests

- Collision tests

Test 5

- Statistical analysis

- Protocol hypothesis refinement

- Search for actual application-layer messages

Current Working Hypothesis

Power-up

↓

Node discovery

↓

Address assignment

↓

Conflict detection

↓

Master/slave election

↓

Show more lines

The current captures appear to be dominated by the discovery/address-management layer rather than pump operating data. The AD.6.5.7 experiments are likely the highest-value tests to perform first.